SPECIFICATION

Section 07900/079500

Previous 05800

Wabo®FlameGuard II– Life Safety Series

Horizontal, Vertical and Underslab Fire Barrier Systems

PART 1 - GENERAL

1.01	Work Included

A.	The work shall consist of furnishing and installing fire barrier assemblies in accordance with the details shown on the plans and the requirements of the specifications.  The fire barrier assemblies are proprietary designs utilizing pre-engineered components and materials tested to meet a required fire endurance rating expressed in hours.

B.	Related Work

- Cast-in-place concrete

- Fire Stopping

- Gypsum Wallboard Construction

- Miscellaneous and ornamental metals

- Flashing and sheet metal

1.02	Submittals

A.	Template Drawings - Submit typical fire barrier cross-section(s) indicating pertinent dimensioning, general construction, and relationship to expansion control system (if applicable).

- Third Party Listing - Submit nationally recognized independent third party published listing or certification letter confirming product to meet required test standard(s) and fire endurance rating(s).

1.03	Product Delivery, Storage and Handling

A.	Deliver products in manufacturer's original carton or labeled containers and store under protective cover in interior dry locations until installed. Protect from weather and construction activities.

1.04	Acceptable Manufacturer

A.	All fire barriers shall be as manufactured/supplied by Sika Emseal, 25 Bridle Lane, Westborough, MA 01581 USA.

B.	Alternate manufacturers and their products will be considered, provided they meet the required fire rating, and are produced of materials that are equal to or superior to those used in the specified fire barrier assembly.

C.	Any proposed alternate systems must be submitted and receive approval 21 days prior to the bid.  All post bid submittals will not be considered.  This submission shall be in accordance with MATERIALS AND SUBSTITUTIONS.

Any manufacturer wishing to submit for prior approval must provide the following:

1.	A working 6” sample of the proposed system with a letter describing how system is considered superior to the specified fire barrier assembly.

2.	A project proposal drawing that illustrates the recommended alternate system installed in the construction that is specific to the project.  Typical catalog cut sections will not be considered.

3.	Nationally recognized third-party listing or certification letter confirming that proposed system meets all required test standards and fire endurance ratings. Manufacturer’s self-written opinion and/or certification letters substituting as third-party certification will not be accepted.

4.	Verifiable list of prior installations showing prior and successful experience with the proposed systems.

5.	Any substitution products not adhering to all specification requirements within, will not be considered.

1.05    Quality Assurance

- Warranty: Standard material limited warranty or project specific warranty available. Installation shall be in strict accordance with manufacturer’s technical specifications, details, installation instructions and general procedures in effect for normal intended usage and suitable applications under specific design movements and loading conditions.

- Manufacturer: Shall have a minimum ten (10) years experience specializing in the design and manufacture of Architectural Expansion Control Systems

- Installation shall be in strict accordance with manufacturer’s technical specifications, details, installation instructions and general procedures in effect for normal intended usage and suitable applications under specified design movements.

- Manufacturer:  Shall have a minimum ten (10) years experience specializing in the design and manufacture of Architectural Expansion Control and Fire Barrier Systems.

- Products: Fire Barrier System shall be installed with manufacturer’s blockout repair materials in horizontal applications.

PART 2 - PRODUCT

2.01	General

A.	Provide factory assembled fire barrier system that has been designed to provide the required fire endurance rating, minimize passage of smoke and accommodate dynamic movement without stress or degradation to its components.  Documentation by a recognized third-party witnessing agency shall certify that the system has been tested and meets the requirements of ASTM E-1966, UL-2079, UBC Section 706, International Building Code Section 712.3 and ICBO ES AC30 for fire endurance. For assurance of movement capability, provide system that meets the requirements of section 2.03 Table I accompanied by third party documentation.

Furnish cycle tested Wabo®FlameGuard II Fire Barrier System for rated openings of 2 inches or wider as supplied by Sika Emseal and as indicated on drawings.

2.02	Components and Materials

A.	Flexible Fire Blanket - Provide high purity ceramic fiber blanket meeting the following requirements. Include integral stainless-steel foil laminate where required to achieve desired fire performance.

Physical Properties				Values

Density						8 PCF (min.)

Thickness					As required

Color						White

Continuous Use Temperature		2,000 – 2,300 deg. F

Smoke Developed (ASTM E-84)		0

Stainless Steel (Type 302) 			2 mil. (thickness)

- Encapsulation (Dust Barrier) - Provide manufacturers standard fabric reinforced aluminum foil.

- Attachment Retainer - Provide preformed 18 ga. (min.) perforated metal profile with manufacturer’s standard assembly hardware and fasteners to provide proper attachment of fire barrier assembly to adjoining construction. Not utilized for 2-inch Wabo®FlameGuard II Horizontal Fire Barrier System.

- Attachment Carrier - Provide high temperature fabric with a nominal thickness of .030” and service temperatures of 1800F and melt temperatures of 3100F. Fabric shall be abrasion resistant with nominal weight of 18 oz per square yard. Utilized for 2-inch Wabo®FlameGuard II Horizontal Fire Barrier System.

- Accessories - Provide necessary and related parts including splice sealants, splice transitions and anchors (excluded for vertical fire barriers) required for complete installation.

2.03	Movement Cycling

Manufacturers Fire Barrier assembly shall demonstrate ability to cycle in accordance with Table I. Fire barrier shall be cycle tested full-length incorporating splice transitions. All cycling and observations shall have been witnessed and documented by an independent third-party testing laboratory.

TABLE I

| Movement Type | Nominal Cycling Rate ( cpm ) | Complete Number of Cycles |
| --- | --- | --- |
| Seismic Followed by: Thermal Total Cycles: | 30 10 | 100 400 500 |

2.04	Fabrication

A.	Fire barrier systems shall be shop assembled and shipped in standard 10-foot lengths.

B.	Splice sealants, transitions and anchoring hardware (excluded for vertical fire barriers) required for complete installation will be shipped as loose components in manufacturer’s standard shipping carton.

C.	Fire barrier systems shall be cut in the field for exact length and changes in direction.

PART 3 - EXECUTION

3.01	Installation

A.	Protect all fire barrier components from damage during storage, installation and post installation activities including placement of expansion control system.

B.	Wabo®FlameGuard II fire barrier assembly shall be installed in strict accordance with manufacturer’s installation procedures along with the advice of their product engineers.

C.	Fire barrier assembly shall be installed in the correct width of opening as called for in the contract plans and third-party listing.  Variations in width shall be brought to the attention of the architect and product manufacturer prior to the installation of any material. Failure to do so may affect certification and fire endurance of assembly.

3.02	Clean and Inspect

- Upon completing installation of the Wabo®FlameGuard II Fire Barrier Assembly, inspect all splices to ensure proper sealants have been applied in sufficient amounts.  Clean and remove any debris that is observed at the base of the fire barrier void prior to installation of expansion joint cover.